## Load Distribution Schedule
LOAD DISTRIBUTION SCHEDULE
PROJECT: UNIVERSITY OF BOLTON | [6 empty] | DB NO: | DB - Ground Floor 01 | [7 empty] | Feed From | S.M.D.B - GF
Rating of Incomer: 63 A TP 150 A TP 100 B
[8 empty] | CONNECTED LOADS / WATTS PER UNIT | [19 empty] | LOAD PER CCT. W |  |  | REMARKS
NUMBER | RATING OF LCB | S.R. CKT NO. | MCB TRIP RATING | CKT WIRE SIZE SQ.MM | ECC WIRE SIZE SQ.MM | CONDUIT SIZE MM | CIRCUIT DESCRIPTION | Extended Outlets | 2 x 200 W SPOT LTS | SPOT LTS | FOCUS LIGHT 150 W | LED LIGHT | CALL BELL | SIGN BOARD | MECHANICAL CALL POINT 100 W | ALARM SOUNDER 10 W | SMOKE & HEAT DETECTOR | 13 A S/O 500 W EACH | 13 A S/O 500 W EACH | AIR CURTAIN | CENTRAL UNIT 300 W | HAND D/L 300 W | SPARE 200 W | EXIT SIGN 200 W | GATE MOTOR / PUMP 1000 W | MIRROR LIGHT 100 W | WATTS PER UNITS | R | Y | B
1 | Sec. 1 40A 4P 100mA | R1 | 16 | 2.5 | 2.5 | 20 | CLASS ROOM-05 |  |  |  |  | 12 | [14 empty] | 35 | 420
2 |  | Y1 | 16 | 2.5 | 2.5 | 20 | CLASS ROOM-04 |  |  |  |  | 12 | [14 empty] | 35 |  | 420
3 |  | B1 | 16 | 2.5 | 2.5 | 20 | CLASS ROOM-03 |  |  |  |  | 12 | [14 empty] | 35 |  |  | 420
4 |  | R2 | 10 | 2.5 | 2.5 | 20 | CLASS ROOM-02 |  |  |  |  | 12 | [14 empty] | 35 | 420
5 |  | Y2 | 10 | 2.5 | 2.5 | 20 | CLASS ROOM-01 |  |  |  |  | 12 | [14 empty] | 35 |  | 420
6 |  | B2 | 10 | 2.5 | 2.5 | 20 | CLASS ROOM-01 |  |  |  |  | 12 | [14 empty] | 35 |  |  | 420
7 |  | R3 |  |  |  |  | CLASS ROOM-CAMERA
8 |  | Y3
9 | Sec. 2 40A 4P 30mA | B3 | 16 | 2.5 | 2.5 | 20 | LOBBY |  |  |  |  | 14 | [14 empty] | 35 |  |  | 490
10 |  | R4 | 32 | 4 | 4 | 20 | CLASS ROOM-06 | [10 empty] | 5 | [8 empty] | 200 | 1000 |  |  | RING CIRCUIT
11 |  | Y4 | 32 | 4 | 4 | 20 | CLASS ROOM-04 | [10 empty] | 5 | [8 empty] | 200 |  | 1000 |  | RING CIRCUIT
12 |  | B4 | 32 | 4 | 4 | 20 | CLASS ROOM-03 | [10 empty] | 5 | [8 empty] | 200 |  |  | 1000 | RING CIRCUIT
13 |  | R5 | 32 | 4 | 4 | 20 | CLASS ROOM-05 | [10 empty] | 5 | [8 empty] | 200 | 1000 |  |  | RING CIRCUIT
14 |  | Y5 | 32 | 4 | 4 | 20 | CLASS ROOM-04 | [10 empty] | 5 | [8 empty] | 200 |  | 1000 |  | RING CIRCUIT
15 |  | B5 | 32 | 4 | 4 | 20 | CLASS ROOM-03 | [10 empty] | 5 | [8 empty] | 200 |  |  | 1000 | RING CIRCUIT
16 |  | R6 | 32 | 4 | 4 | 20 | CLASS ROOM-02 | [10 empty] | 5 | [8 empty] | 200 | 1000 |  |  | RING CIRCUIT
17 |  | Y6 | 32 | 4 | 4 | 20 | CLASS ROOM-01 | [10 empty] | 5 | [8 empty] | 200 |  | 1000 |  | RING CIRCUIT
18 |  | B6 | 32 | 4 | 4 | 20 | COMMON AREA | [10 empty] | 6 | [8 empty] | 200 |  |  | 1200 | RING CIRCUIT
19 | Sec. 3 40A 4P 30mA | R7 | 32 | 4 | 4 | 20 | CLASS ROOM-02 | [10 empty] | 5 | [8 empty] | 200 | 1000 |  |  | RING CIRCUIT
20 |  | Y7 | 32 | 4 | 4 | 20 | CLASS ROOM-01 | [10 empty] | 5 | [8 empty] | 200 |  | 1000 |  | RING CIRCUIT
21 |  | B7 | 32 | 4 | 4 | 20 | PASSAGE | [10 empty] | 4 | [8 empty] | 200 |  |  | 800 | RING CIRCUIT
22 | Sec. 4 40A 4P 30mA | R8 | 32 | 4 | 4 | 20 | 2 C WATER HEATER | [13 empty] | 1 | [5 empty] | 3000 | 3000
23 |  | Y8
24 |  | B8
[12 empty] | 86 | [5 empty] | 60 |  |  | 1
[28 empty] | 7840 | 4840 | 5330
[28 empty] | 7.84 | 4.84 | 5.33
CABLE SIZE: 4 x 16 sq.mm PVC / XLPE / SWA Cu. + 1 x 10 sq.mm Cu, PVC ECC | [15 empty] | TOTAL LOAD | [14 empty] | 18.010 KW